{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["Test report of anti-static f..."],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Test report of anti-static f...","index":0,"n_rows":18,"n_cols":7,"rows_kept":18,"merged":[[0,0,0,6],[2,0,9,0],[2,1,9,1],[2,2,9,2],[10,0,17,0],[10,1,17,1],[10,2,17,2]],"flags":["formulas_cached_only"]}
["Conductivefloor Technical Parameters"]
["Presentation","Detection category","Testing Agency","Test items","Test basis/test method","Scope of the report","Test results"]
[1,"Detection of anti-static PVC coiled material","Information Industry Anti-static Product Quality Supervision and Testing Center","Surface resistance","SJ/T 11236-2001","Static conductive type: < 1 * 106Ω Static dissipation: 1 * 106~ 109Ω","6.81*105Ω"]
[{"$nulls":3},"Volume resistance","SJ/T 11236-2001","Static conductive type: < 1 * 106Ω Static dissipation: 1 * 106~ 109Ω","2.85*105Ω"]
[{"$nulls":3},"Abrasion loss","SJ/T 11236-2001","Not more than 0.020 G/cm3",0.014]
[{"$nulls":3},"Electrostatic decay period","GJB 3007A-2009","±1000~±100V  ≤2S","+V0.2 -V0.2"]
[{"$nulls":3},"Triboelectrification voltage","SJ/T 10694-2006","｜U｜＜100V",40]
[{"$nulls":3},"Residual concavity","SJ/T 11236-2001","≤0.15mm",0.09]
[{"$nulls":3},"Heating dimensional change rate","SJ/T 11236-2001","≤0.20%","Horizontal 0.09% Vertical 0.04%"]
[{"$nulls":3},"Combustion performance",null,null,"Total afterflame time 35/S"]
[2,"Anti-static PVC floor (ESD series)","Information Industry Anti-static Product Quality Supervision and Testing Center","Point-to-point resistance","SJ/T 11236-2001","Static conductive type: < 1 * 106Ω Static dissipation: 1 * 106~ 109Ω","4.54*105Ω"]
[{"$nulls":3},"Volume resistance","SJ/T 11236-2001","Static conductive type: < 1 * 106Ω Static dissipation: 1 * 106~ 109Ω","3.07*105Ω"]
[{"$nulls":3},"Combustion performance","SJ/T 11236-2001","FV-0 ≤ 10S","8.60S, FV-0 compliant"]
[{"$nulls":3},"Abrasion loss","SJ/T 11236-2001","Not more than 0.020 G/cm3",0.015]
[{"$nulls":3},"Electrostatic decay period","GJB 3007A-2009","±1000~±100V  ≤2S","+V0.2 -V0.1"]
[{"$nulls":3},"Triboelectrification voltage","SJ/T 10694-2006","｜U｜＜100V",70]
[{"$nulls":3},"Heating dimensional change rate","SJ/T 11236-2001","≤0.20%",0.08]
[{"$nulls":3},"Concave degree","SJ/T 11236-2001","≤ 0.30mm at 23 ℃, ≤ 0.60mm at 45 ℃","0.18 mm at 23 ℃, 0.37 mm at 45 ℃"]